## Circular Manning
Circular Manning
http://en.wikipedia.org/wiki/Manning_formula | [5 empty] | 1 |  | cm
General formula is Q=A*k/n*Rh^(2/3)*S^0.5 | [5 empty] | 0.0254 |  | meter
Circular pipe formula - see at the left |  |  |  |  | R in meter | 50 |  | inch
| Units are [Q]=CFS [h]=feet [L]=feet |  |  |  | H in meter | 0.762 |  | feet
[6 empty] | arg | 0.98476
|  |  |  | select unit |  | theta | 0.17481
Enter DIAMETER of pipe |  |  | 100 | meter |  | A | 8.8486
Enter level |  |  | 30 | inch |  | P | 17.4808
Enter slope |  |  | 10% |  |  | Rh | 0.50619
Enter roughness (0.001…0.2) |  |  | 0.01 |  |  | Q(m3s) | 177.7267
Flow | 6276.3488 | CFS |  |  |  | Q(m3h) | 639816.2735
| 376580.9295 | CFM
| 22594855.7718 | CFH
| 2817013.6434 | GPM
| 4056.4996 | MGD
| 2347511.3695 | IGPM
| 639816273.4905 | LPH
| 10663604.5582 | LPM
| 177726.7426 | LPS
| 639816.2735 | M3H

## Parshall
| PARSHALL FLUME | [6 empty] | Dif | THROAT(") | C | α
www.usbr.gov/pmts/hydraulics_lab/pubs/wmm/chap08_10.html | [6 empty] | 6 | -11 | 1 | 0.338 | 1.55
| Formula is Q=C*h^α | [5 empty] | 12 | -10 | 2 | 0.676 | 1.55
| Units are [Q]=CFS [h]=feet | [5 empty] | 24 | -9 | 3 | 0.992 | 1.55
[5 empty] | select unit | 3.95 | 3.95 | -6 | 6 | 2.06 | 1.58
| Enter throat width |  |  | 12 | inch |  | 8 | -3 | 9 | 3.07 | 1.53
| Enter level |  |  | 20 | cm | 1.55 | 1.55 | 0 | 12 | 3.95 | 1.55
[7 empty] | 1.55 | 12 | 24 | 8 | 1.55
| Flow | 2.0558 | CFS |  |  | 2.0558 |  | 24 | 36 | 12 | 1.57
|  | 123.345 | CFM |  |  |  |  | 36 | 48 | 16 | 1.58
|  | 7400.7017 | CFH |  |  | cm |  | 48 | 60 | 20 | 1.59
[6 empty] | meter |  | 60 | 72 | 24 | 1.59
|  | 922.6825 | GPM |  |  | inch |  | 72 | 84 | 28 | 1.6
|  | 1.3287 | MGD |  |  | feet |  | 84 | 96 | 32 | 1.61
|  | 768.9021 | IGPM |  |  |  |  | 108 | 120 | 39.38 | 1.6
[6 empty] | 0.083333 | 12 | 132 | 144 | 46.75 | 1.6
|  | 209564.9297 | LPH |  |  | 0.032808 | 0.65617 | 168 | 180 | 57.81 | 1.6
|  | 3492.7488 | LPM |  |  |  |  | 228 | 240 | 76.25 | 1.6
|  | 58.2125 | LPS |  |  |  |  | 288 | 300 | 94.69 | 1.6
[8 empty] | 348 | 360 | 113.13 | 1.6
|  | 209.5649 | M3H |  |  |  |  | 468 | 480 | 150 | 1.6
[8 empty] | 588 | 600 | 186.88 | 1.6

## V-Notch
| V-Notch Sharp Crest | [6 empty] | cm
www.engineeringexcelspreadsheets.com/?p=221 |  |  |  |  | k | 0.0044303 | 0.032808 | meter
| Formula is Q=4.28*C*tg(Θ/2)*(h+k)^2.5 |  |  |  | c | 0.5787 | 1.9685 | inch
| Units are [Q]=CFS [h]=feet |  |  |  | Q | 6.3147 |  | feet
Enter angle (degree) |  |  | 50
Enter level |  |  | 60 | cm
Flow | 6.3147 | CFS
| 378.8818 | CFM
| 22732.9065 | CFH
| 2834.2251 | GPM
| 4.0813 | MGD
| 2361.8543 | IGPM
| 643725.4421 | LPH
| 10728.7574 | LPM
| 178.8126 | LPS
| 643.7254 | M3H

## Cipolletti
Trapezoidal Cipolletti Sharp Crest
www.lmnoeng.com/Weirs/cipoletti.htm |  |  |  |  | L | 1.3333 | 0.083333 | cm
| Formula is Q=3.367*L*h^1.5 |  |  |  | h | 0.98425 | 0.032808 | meter
| Units are [Q]=CFS [h]=feet [L]=feet | [6 empty] | inch
[5 empty] | Q | 4.3837 |  | feet
Select units
Enter crest length |  |  | 16 | inch
Enter level |  |  | 30 | cm
Flow | 4.3837 | CFS
| 263.0223 | CFM
| 15781.3369 | CFH
| 1967.5382 | GPM
| 2.8333 | MGD
| 1639.6152 | IGPM
| 446878.5409 | LPH
| 7447.9757 | LPM
| 124.1329 | LPS
| 446.8785 | M3H

## Rectangular contracted
Rectangular contracted Sharp Crest
www.flowsizer.com/content/rectangular-contracted-weir-calculator |  |  |  |  | L | 1.3123 | 0.032808 | cm
Formula is Q=Q = 3.247*L*h^1.48-(0.566*(l*h)^1.9)/(1+2*L^1.8) |  |  |  |  | h | 0.98425 | 0.032808 | meter
| Units are [Q]=CFS [h]=feet [L]=feet | [6 empty] | inch
[5 empty] | Q(CFS) | 3.9463 |  | feet
Select units
Enter crest length |  |  | 40 | cm
Enter level |  |  | 30 | cm
Flow | 3.9463 | CFS
| 236.7755 | CFM
| 14206.5285 | CFH
| 1771.1989 | GPM
| 2.5505 | MGD
| 1475.9991 | IGPM
| 402284.848 | LPH
| 6704.7475 | LPM
| 111.7458 | LPS
| 402.2848 | M3H

## Rectangular suppressed
Rectangular Suppressed Sharp Crest
www.usbr.gov/pmts/hydraulics_lab/pubs/wmm/ |  |  |  |  | L | 9.8425 | 0.032808 | cm
| Formula is Q=Q = 3.33*L*h^1.5 |  |  |  | h | 0.98425 | 0.032808 | meter
| Units are [Q]=CFS [h]=feet [L]=feet | [6 empty] | inch
[5 empty] | Q(CFS) | 32.0044 |  | feet
Select units
Enter crest length |  |  | 300 | cm
Enter level |  |  | 30 | cm
Flow | 32.0044 | CFS
| 1920.2652 | CFM
| 115215.9127 | CFH
| 14364.5439 | GPM
| 20.6849 | MGD
| 11970.4533 | IGPM
| 3262557.4882 | LPH
| 54375.9581 | LPM
| 906.266 | LPS
| 3262.5575 | M3H

## Palmer Bowlus
| Palmer Bowlus Flume | [7 empty] | Diam Width | C | b | α
www.plasti-fab.com/sites/www.plasti-fab.com/files/document-center/PalmerBowlusFlume-FlowEquations.pdf | [7 empty] | 15 | 4 | 1.73 | 0.00588 | 1.9573
| Formula is Q=C*(h+b)^α |  |  |  |  | 1 | 0 | 60 | 6 | 2.071 | 0.005421 | 1.9025
| Units are [Q]=CFS [h]=feet | [6 empty] | 16 | 8 | 2.537 | 0.1456 | 1.9724
[5 empty] | select unit | 0 | 12 | 72 | 10 | 2.843 | 0.0161 | 1.953
| Enter diameter width |  |  | 5 | feet |  |  | 15 | 12 | 3.142 | 0.017 | 1.9362
| Enter level |  |  | 40 | cm | 7.839 | 7.183 | C | 15 | 3.574 | 0.01682 | 1.9062
[6 empty] | 0.155 | 0.126 | b | 18 | 3.988 | 0.01875 | 1.8977
| Flow | 14.7703 | CFS |  |  | 1.9871 | 1.9833 | α | 21 | 4.223 | 0.039 | 1.9619
|  | 886.22 | CFM |  |  | 16.7947 | Q(CFS) | 14.7703 | 24 | 4.574 | 0.0408 | 1.9497
|  | 53173.1973 | CFH |  |  | 14.7703 | cm |  | 27 | 4.97 | 0.038 | 1.9269
[7 empty] | meter |  | 30 | 5.022 | 0.0625 | 1.9663
|  | 6629.3684 | GPM |  |  |  | inch |  | 36 | 5.462 | 0.08 | 1.991
|  | 9.5463 | MGD |  |  |  | feet |  | 42 | 6.12 | 0.078 | 1.9628
|  | 5524.4736 | IGPM |  |  |  |  | 60 | 48 | 6.626 | 0.085 | 1.9586
[7 empty] | 1 | 5 | 60 | 7.183 | 0.126 | 1.9833
|  | 1505700.1156 | LPH |  |  |  | 0.032808 | 1.3123 | 72 | 7.839 | 0.155 | 1.9871
|  | 25095.0019 | LPM
|  | 418.25 | LPS
|  | 1505.7001 | M3H

## H-Flume
| H Flume | [7 empty] | Depth | A | B | C
www2.alterra.wur.nl/Internet/webdocs/ilri-publicaties/publicaties/Pub20/pub20-h7.2.pdf | [7 empty] | 7 | 0.5 | 0.0372 | 2.6629 | 0.1954
| Formula is Q=A+B*LOG(h)+C*(LOG(h))^2 |  |  |  |  | 0.33333 | 1 | 3 | 0.75 | 0.0351 | 2.6434 | 0.2243
| Units are [Q]=M3S [h]=meter | [6 empty] | 8 | 1 | 0.0206 | 2.5902 | 0.2281
[5 empty] | select unit | 0.66667 | 0.5 | 4.5 | 1.5 | 0.0238 | 2.5473 | 0.254
| Enter Depth |  |  | 4 | feet |  |  | 8 | 2 | 0.0237 | 2.4918 | 0.2605
| Enter level |  |  | 26.2 | cm | 0.0588 | 0.0329 | A | 2.5 | 0.0268 | 2.4402 | 0.26
[6 empty] | 2.3032 | 2.3977 | B | 3 | 0.0329 | 2.3977 | 0.2588
| Flow | 2.1294 | CFS |  |  | 0.2547 | 0.2588 | C | 4.5 | 0.0588 | 2.3032 | 0.2547
|  | 127.7643 | CFM |  |  | -1.1948 |  | -1.2743
|  | 7665.8601 | CFH |  |  | 63.858 | cm | 53.178 | 60.298 | Q(LPS)
[7 empty] | meter |  | 2.1294 | Q(CFS)
|  | 955.7411 | GPM |  |  |  | inch
|  | 1.3763 | MGD |  |  |  | feet
|  | 796.4509 | IGPM |  |  |  |  | 4
[7 empty] | 0.3048 | 1.2192
|  | 217072.7788 | LPH |  |  |  | 0.01 | 0.262
|  | 3617.8796 | LPM
|  | 60.298 | LPS
|  | 217.0728 | M3H

## Khafagi
Khafagi Venturi Flume
www.inducont.lv/tools/download.php?name=venturi_teknes.pdf |  |  |  |  | L(meter) | 0.12 | 0.01 | meter
| Formula is Q=6278*b*h^1.5 + 328*h^2.5 |  |  |  | h(meter) | 0.2 | 0.01 | cm
| Units are [Q]=M3H [h]=meter [L]=meter | [6 empty] | inch
[5 empty] | Q(M3H) | 73.25 |  | feet
[5 empty] | Q(CFS) | 0.71856
Select units
Enter throat width |  |  | 12 | cm
Enter level |  |  | 20 | cm
Flow | 0.71856 | CFS
| 43.1133 | CFM
| 2586.7999 | CFH
| 322.5093 | GPM
| 0.46441 | MGD
| 268.7577 | IGPM
| 73250.0092 | LPH
| 1220.8335 | LPM
| 20.3472 | LPS
| 73.25 | M3H

## Leopold
Leopold Lagco Flume
www.inducont.lv/tools/download.php?name=venturi_teknes.pdf |  |  |  |  | b(meter) | 1.524 | 0.3048 | meter
www.ceaeq.gouv.qc.ca/documents/publications/echantillonnage/debit_conduit_ouv_C7_ang.pdf | [7 empty] | cm
| Formula is Q=1329.4 * D^0.953 * h^1.547 |  |  |  | h(meter) | 0.4 | 0.01 | inch
| Units are [Q]=LPS [h]=meter [L]=meter | [6 empty] | feet
[5 empty] | Q(LPS) | 481.3125
[5 empty] | Q(CFS) | 16.9974
Select units
Enter pipe diameter |  |  | 5 | feet
Enter level |  |  | 40 | cm
[6 empty] | 152 | 221.25 | 1332.2519
Flow | 16.9974 | CFS |  |  |  | 203 | 291.02 | 1330.0841
| 1019.8436 | CFM |  |  |  | 254 | 360 | 1328.9112
| 61190.6135 | CFH |  |  |  | 305 | 420.004 | 1302.3139
[6 empty] | 381 | 529.8 | 1328.8943
| 7628.9397 | GPM |  |  |  | 457 | 630.32 | 1329.4161
| 10.9857 | MGD |  |  |  | 533 | 730.074 | 1329.8292
| 6357.4498 | IGPM |  |  |  | 610 | 829.15 | 1328.048
[6 empty] | 762 | 1025.63 | 1328.8857
| 1732725.0552 | LPH |  |  |  | 914 | 1220.24 | 1329.4241
| 28878.7509 | LPM |  |  |  | 1067 | 1413.35 | 1328.6452
| 481.3125 | LPS |  |  |  | 1219 | 1605.15 | 1329.0891
[7 empty] | K | 1329.4072
| 1732.7251 | M3H